Specifications

| Nominal Voltage |  |  | 12 V |
| --- | --- | --- | --- |
| Capacity (25℃) | 20HR(10.5V) |  | 3.6Ah |
|  | 10HR(10.5V) |  | 3.3Ah |
|  | 1HR(9.60V) |  | 2.3Ah |
| Dimension | Length |  | 90±1mm (3.54inch) |
|  | Width |  | 70±1mm (2.76inch) |
|  | Height |  | 101±1mm (3.98inch) |
|  | Total Height |  | 107±1mm (4.21inch) |
| Approx. Weight |  |  | 1.3kg (2.87lbs)±5% |
| Terminal type |  |  | F1/F2 |
| Internal resistance (Fully charged, 25℃) |  |  | Approx. 58mΩ |
| Capacity affected by temperature (20HR) |  | 40℃ | 102% |
|  |  | 25℃ | 100% |
|  |  | 0℃ | 85% |
|  |  | -15℃ | 65% |
| Self-discharge (25℃) |  | 3 month | Remaining Capacity: 91% |
|  |  | 6 month | Remaining Capacity: 82% |
|  |  | 12 month | Remaining Capacity: 65% |
| Nominal operating temperature |  |  | 25℃±3℃(77℉±5℉) |
| Operating temperature range |  | Discharge | -15℃～50℃(5℉～122℉) |
|  |  | Charge | -10℃～50℃(14℉～122℉) |
|  |  | Storage | -20℃～50℃(-4℉～122℉) |
| Float charging voltage(25℃) |  |  | 13.60 to 13.80V Temperature compensation: -18mV/℃ |
| Cyclic charging voltage(25℃) |  |  | 14.50 to 15.00V Temperature compensation: -30mV/℃ |
| Maximum charging current |  |  | 1.08A |
| Maximum discharge current |  |  | 54A(5 sec.) |
| Designed floating life(20℃) |  |  | 5 years |

Dimensions

Terminal

Constant Current Discharge Characteristics (A, 25℃)

| F.V/TIME | 5min | 10min | 15min | 30min | 60min | 2h | 3h | 4h | 5h | 10h | 20h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 9.60V | 13.8 | 8.71 | 6.80 | 3.83 | 2.36 | 1.29 | 0.89 | 0.74 | 0.63 | 0.34 | 0.18 |
| 9.90V | 13.3 | 8.45 | 6.64 | 3.75 | 2.32 | 1.28 | 0.89 | 0.73 | 0.62 | 0.34 | 0.18 |
| 10.2V | 12.8 | 8.10 | 6.40 | 3.65 | 2.27 | 1.27 | 0.88 | 0.72 | 0.62 | 0.34 | 0.18 |
| 10.5V | 12.2 | 7.76 | 6.17 | 3.55 | 2.22 | 1.25 | 0.87 | 0.72 | 0.61 | 0.33 | 0.18 |
| 10.8V | 11.5 | 7.32 | 5.85 | 3.42 | 2.15 | 1.22 | 0.85 | 0.70 | 0.59 | 0.33 | 0.17 |

Constant Power Discharge Characteristics (Watt, 25℃)

| F.V/TIME | 5min | 10min | 15min | 30min | 60min | 2h | 3h | 4h | 5h | 10h | 20h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 9.60V | 153.9 | 98.1 | 77.6 | 43.9 | 27.3 | 15.1 | 10.6 | 8.79 | 7.50 | 4.10 | 2.20 |
| 9.90V | 148.5 | 95.4 | 75.7 | 43.0 | 26.9 | 15.0 | 10.5 | 8.74 | 7.45 | 4.08 | 2.19 |
| 10.2V | 143.1 | 91.8 | 72.9 | 41.8 | 26.2 | 14.8 | 10.4 | 8.68 | 7.40 | 4.06 | 2.17 |
| 10.5V | 136.8 | 87.5 | 70.5 | 40.8 | 25.7 | 14.7 | 10.3 | 8.62 | 7.35 | 4.03 | 2.16 |
| 10.8V | 128.7 | 82.5 | 66.7 | 39.2 | 24.9 | 14.3 | 10.1 | 8.36 | 7.13 | 3.95 | 2.11 |

Note: The above characteristics data can be obtained within three charge/discharge cycles.

Construction

| Component | Positive plate | Negative plate | Container | Cover | Separator | Electrolyte | Safety valve | Terminal |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Raw material | Lead dioxide | Lead | ABS | ABS | AGM | Sulfuric acid | Rubber | Copper |

Discharge Characteristics(25℃)

The Relationship for Open Circuit Voltage and Residual Capacity (25℃)

Floating Life on Temperature

Effect of Temperature on Capacity

Charging Characteristics(25℃)

The Relationship for Charging Voltage and Temperature

Cycle Life on D.O.D(25℃)

Self-discharge Characteristics

www.huaxiangbattery.com