Specifications

| Nominal Voltage |  |  | 12 V |
| --- | --- | --- | --- |
| Capacity (25℃) | 20HR(10.5V) |  | 24 Ah |
|  | 10HR(10.5V) |  | 22.4Ah |
|  | 1HR(9.60V) |  | 15.2Ah |
| Dimension | Length |  | 166±2mm (6.54inch) |
|  | Width |  | 175±2mm (6.89inch) |
|  | Height |  | 125±2mm (4.92inch) |
|  | Total Height |  | 125±2mm (4.92inch) |
| Approx. Weight |  |  | 7.6kg (16.74lbs)±5% |
| Terminal type |  |  | F17/F18 |
| Internal resistance (Fully charged, 25℃) |  |  | Approx. 15mΩ |
| Capacity affected by temperature (20HR) |  | 40℃ | 102% |
|  |  | 25℃ | 100% |
|  |  | 0℃ | 85% |
|  |  | -15℃ | 65% |
| Self-discharge (25℃) |  | 3 month | Remaining Capacity: 91% |
|  |  | 6 month | Remaining Capacity: 82% |
|  |  | 12 month | Remaining Capacity: 65% |
| Nominal operating temperature |  |  | 25℃±3℃(77℉±5℉) |
| Operating temperature range |  | Discharge | -15℃～50℃(5℉～122℉) |
|  |  | Charge | -10℃～50℃(14℉～122℉) |
|  |  | Storage | -20℃～50℃(-4℉～122℉) |
| Float charging voltage(25℃) |  |  | 13.60 to 13.80V Temperature compensation: -18mV/℃ |
| Cyclic charging voltage(25℃) |  |  | 14.50 to 15.00V Temperature compensation: -30mV/℃ |
| Maximum charging current |  |  | 7.2A |
| Maximum discharge current |  |  | 360A(5 sec.) |
| Designed floating life(20℃) |  |  | 5 years |

Dimensions

Terminal

Constant Current Discharge Characteristics (A, 25℃)

| F.V/TIME | 10min | 15min | 30min | 60min | 2h | 3h | 4h | 5h | 8h | 10h | 20h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 9.60V | 56.3 | 44.0 | 24.8 | 15.2 | 8.60 | 5.95 | 4.92 | 4.19 | 2.72 | 2.27 | 1.22 |
| 9.90V | 54.6 | 42.9 | 24.3 | 15.0 | 8.55 | 5.91 | 4.89 | 4.16 | 2.70 | 2.26 | 1.21 |
| 10.2V | 52.4 | 41.4 | 23.6 | 14.6 | 8.47 | 5.87 | 4.86 | 4.13 | 2.68 | 2.25 | 1.21 |
| 10.5V | 50.1 | 40.0 | 23.0 | 14.3 | 8.34 | 5.83 | 4.82 | 4.10 | 2.66 | 2.24 | 1.20 |
| 10.8V | 47.3 | 37.8 | 22.1 | 13.9 | 8.13 | 5.66 | 4.68 | 3.98 | 2.58 | 2.19 | 1.18 |

Constant Power Discharge Characteristics (Watt, 25℃)

| F.V/TIME | 10min | 15min | 30min | 60min | 2h | 3h | 4h | 5h | 8h | 10h | 20h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 9.60V | 635 | 502 | 284 | 177 | 101 | 70.7 | 58.6 | 50.0 | 32.6 | 27.3 | 14.6 |
| 9.90V | 616 | 490 | 278 | 174 | 100 | 70.3 | 58.3 | 49.7 | 32.4 | 27.2 | 14.6 |
| 10.2V | 591 | 471 | 270 | 170 | 99.1 | 69.8 | 57.9 | 49.3 | 32.2 | 27.0 | 14.5 |
| 10.5V | 566 | 455 | 263 | 166 | 97.6 | 69.3 | 57.5 | 49.0 | 32.0 | 26.9 | 14.4 |
| 10.8V | 534 | 431 | 254 | 161 | 95.2 | 67.2 | 55.7 | 47.5 | 31.0 | 26.3 | 14.1 |

Note: The above characteristics data can be obtained within three charge/discharge cycles.

Construction

| Component | Positive plate | Negative plate | Container | Cover | Separator | Electrolyte | Safety valve | Terminal |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Raw material | Lead dioxide | Lead | ABS | ABS | AGM | Sulfuric acid | Rubber | Copper |

Discharge Characteristics(25℃)

The Relationship for Open Circuit Voltage and Residual Capacity (25℃)

Floating Life on Temperature

Effect of Temperature on Capacity

Charging Characteristics(25℃)

The Relationship for Charging Voltage and Temperature

Cycle Life on D.O.D(25℃)

Self-discharge Characteristics

www.huaxiangbattery.com