Specifications

| Nominal Voltage |  |  | 12 V |
| --- | --- | --- | --- |
| Capacity (25℃) | 20HR(10.5V) |  | 9.0Ah |
|  | 10HR(10.5V) |  | 8.4Ah |
|  | 1HR(9.60V) |  | 5.9Ah |
| Dimension | Length |  | 151±1.5mm (5.94inch) |
|  | Width |  | 65±1mm (2.56inch) |
|  | Height |  | 94±1mm (3.70inch) |
|  | Total Height |  | 100±1mm (3.94inch) |
| Approx. Weight |  |  | 2.7kg (5.95lbs)±5% |
| Terminal type |  |  | F1/F2 |
| Internal resistance (Fully charged, 25℃) |  |  | Approx. 20mΩ |
| Capacity affected by temperature (20HR) |  | 40℃ | 102% |
|  |  | 25℃ | 100% |
|  |  | 0℃ | 85% |
|  |  | -15℃ | 65% |
| Self-discharge (25℃) |  | 3 month | Remaining Capacity: 91% |
|  |  | 6 month | Remaining Capacity: 82% |
|  |  | 12 month | Remaining Capacity: 65% |
| Nominal operating temperature |  |  | 25℃±3℃(77℉±5℉) |
| Operating temperature range |  | Discharge | -15℃～50℃(5℉～122℉) |
|  |  | Charge | -10℃～50℃(14℉～122℉) |
|  |  | Storage | -20℃～50℃(-4℉～122℉) |
| Float charging voltage(25℃) |  |  | 13.60 to 13.80V Temperature compensation: -18mV/℃ |
| Cyclic charging voltage(25℃) |  |  | 14.50 to 15.00V Temperature compensation: -30mV/℃ |
| Maximum charging current |  |  | 2.7A |
| Maximum discharge current |  |  | 135A(5 sec.) |
| Designed floating life(20℃) |  |  | 5 years |

Dimensions

Terminal

Constant Current Discharge Characteristics (A, 25℃)

| F.V/TIME | 5min | 10min | 15min | 30min | 60min | 2h | 3h | 4h | 5h | 10h | 20h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 9.60V | 34.4 | 21.8 | 17.0 | 9.59 | 5.90 | 3.22 | 2.23 | 1.85 | 1.57 | 0.85 | 0.46 |
| 9.90V | 33.3 | 21.1 | 16.6 | 9.39 | 5.81 | 3.21 | 2.22 | 1.83 | 1.56 | 0.85 | 0.45 |
| 10.2V | 32.0 | 20.3 | 16.0 | 9.11 | 5.66 | 3.18 | 2.20 | 1.82 | 1.55 | 0.84 | 0.45 |
| 10.5V | 30.6 | 19.4 | 15.4 | 8.89 | 5.55 | 3.13 | 2.19 | 1.81 | 1.54 | 0.84 | 0.45 |
| 10.8V | 28.9 | 18.3 | 14.6 | 8.56 | 5.38 | 3.05 | 2.12 | 1.75 | 1.49 | 0.82 | 0.44 |

Constant Power Discharge Characteristics (Watt, 25℃)

| F.V/TIME | 5min | 10min | 15min | 30min | 60min | 2h | 3h | 4h | 5h | 10h | 20h |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 9.60V | 384 | 246 | 194 | 110 | 68.3 | 37.7 | 26.5 | 22.0 | 18.7 | 10.2 | 5.48 |
| 9.90V | 372 | 238 | 189 | 108 | 67.2 | 37.5 | 26.3 | 21.8 | 18.6 | 10.2 | 5.46 |
| 10.2V | 357 | 228 | 182 | 104 | 65.5 | 37.2 | 26.2 | 21.7 | 18.5 | 10.1 | 5.43 |
| 10.5V | 341 | 219 | 176 | 102 | 64.2 | 36.6 | 26.0 | 21.5 | 18.4 | 10.1 | 5.40 |
| 10.8V | 322 | 206 | 167 | 98.1 | 62.3 | 35.7 | 25.2 | 20.9 | 17.8 | 9.87 | 5.29 |

Note: The above characteristics data can be obtained within three charge/discharge cycles.

Construction

| Component | Positive plate | Negative plate | Container | Cover | Separator | Electrolyte | Safety valve | Terminal |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Raw material | Lead dioxide | Lead | ABS | ABS | AGM | Sulfuric acid | Rubber | Copper |

Discharge Characteristics(25℃)

The Relationship for Open Circuit Voltage and Residual Capacity (25℃)

Floating Life on Temperature

Effect of Temperature on Capacity

Charging Characteristics(25℃)

The Relationship for Charging Voltage and Temperature

Cycle Life on D.O.D(25℃)

Self-discharge Characteristics

www.huaxiangbattery.com